| 1.0 | OBJECTIVE : | To lay down the procedure for Microbial monitoring of Manufacturing area, Microbiological lab, Dispensing area and Aseptic area by Settle Plate Method, Air Sampler, Swab Test, Personnel Monitoring and Finger Dab Method. |
| --- | --- | --- |
| 2.0 | SCOPE : | This procedure is applicable for microbial monitoring of Production area and Microbiology area by Settle Plate Method, Air Sampler, Swab Test, Personnel Monitoring and Finger Dab Method at Indiana Ophthalmics LLP. |
| 3.0 | RESPONSIBILITY : | Microbiologist, Microbiology Officer, Microbiology Head |
| 4.0 | ACCOUNTABILITY : | QA Head |
| 5.0 | PROCEDURE : |  |
| 5.1 | Microbial Monitoring of Aseptic area by Settle Plate Method :- |  |
| 5.1.1 | Prepare the Soyabean casein digest agar plates as per SOP No. QAMI18. Use 90 mm petri plates. |  |
| 5.1.2 | Mop outer surface of plate with 70% v/v Isopropyl Alcohol. Mark each Soyabean casein digest agar plate with serial number of location and date of exposure on the bottom side of plate. Record exposure date, time of exposure, site of exposure and activity in respective Annexures (Annexure - I, II, III, IV, V, VI, VII, VIII). |  |
| 5.1.3 | Place all marked plates in petri plate carrier / SS container, mop the outside of petri plate carrier with 70% v/v Isopropyl Alcohol, and transfer to production area or respective exposing area. |  |
| 5.1.4 | Enter the aseptic area of microbiology lab and production department as per entry procedure of respective department. |  |
| 5.1.5 | Carefully open and keep petri plate at site (Annexure - I, II, III, IV, V, VI, VII, VIII) as per marking on the plate, in a slanting position (at about 30 angle) near riser and in horizontal position under Laminar Air Flow. |  |
| 5.1.6 | Expose the petri plates for 4 hours, and then close the lid of petri plates. Keep the plates in the petri plate carrier and transfer to Microbiology lab for incubation. |  |
| 5.1.6.1 | If there is unavailability of stand, expose the plates on floor at the specified location. |  |
| 5.1.6.2 | Individual settle plates shall exposed for not less than two hours in Grade A, B, C and D areas. Settle plates in Grade-A filling area must be exposed during entire filling activity. |  |
| 5.1.7 | Incubate all exposed petri plates at 20-25°C temperature for 72 hours (3 days). After completion of 72 hours, observe and transfer all petri plates at 30-35°C for 48 hours (2 days) in inverted position. |  |
| 5.1.8 | After incubation observe the plates and count the number of colonies. Record in respective format (Annexure - I, II, III, IV, V, VI, VII, VIII). |  |
| 5.1.9 | If the count lies in the Alert / Action limit as specified in the Table-1 & Table-2, microbiologist shall show the plates to Microbiology Head. It should be informed to QA department for further action through ‘Warning Letter’ as per Annexure - XX. |  |
| 5.1.10 | Limit of Bacterial colonies / 4 Hrs. / Plate are as per below Table-1 :- |  |
|  | Table-1:- (Limit of Bacterial Colonies) |  |
|  | Grade; Alert; Action; Specification. A; <1; <1; <1. B; 3; 4; 5. C; 30-44; 45-49; 50. D; 60-94; 95-99; 100. |
| 5.1.11 | Limit of Fungal colonies / 4 Hrs. / Plate are as per below Table-2 :- |  |
|  | Table-2:- (Limit of Fungal Colonies) |  |
|  | Grade; Alert; Action; Specification. A, B, C & D; <1; <1; <1. |
| 5.1.12 | Frequency: - Whenever production is going on / whenever testing is going on (Daily for Grade A, B and C & weekly for Grade D). - In case if area remains shut down for more than 2 consecutive days, then microbial monitoring shall be performed from 3rd day. |  |
| 5.2 | Microbial Monitoring by Air Sampler :- |  |
| 5.2.1 | Follow the SOP No. QAMI56 (Environment Monitoring of Aseptic Area by Air Sampling) for air sampling. |  |
| 5.3 | Contact Plate test of Critical surfaces in aseptic areas of Ophthalmic Department, Drop Department, Veterinary Department and Microbiology Lab :- |  |
| 5.3.1 | Prepare the Dey-Engley Neutralizing agar as per SOP No. QAMI18. Use 55 mm (RODAC) petri plates. |  |
| 5.3.2 | Label the petri plates indicating the surfaces to be tested as per specified in Annexure - IX, X, XI, XII and XIII. |  |
| 5.3.3 | Aseptically transfer the plates to respective area, where the sampling to be carried out. |  |
| 5.3.4 | Aseptically open the contact plates and gently touch on the sampling surface to be mentioned in respective formats. |  |
| 5.3.5 | Clean the tested surfaces with 70% v/v Isopropyl alcohol. |  |
| 5.3.6 | Incubate the petri plates at 20-250C temperature for 72 hours (3 days). After completion of 72 hours, transfer all petri plates at 30-350C for 48 hours (2 days) in inverted position. |  |
| 5.3.7 | After incubation, count the number of colonies and record the results in specified format (Annexure - IX, X, XI, XII and XIII). |  |
| 5.3.8 | If the count lies in the Alert / Action limit as specified in the Table-3 & Table-2, microbiologist shall show the plates to Microbiology Head. It should be informed to QA department for further action through ‘Warning Letter’ as per Annexure - XX. |  |
| 5.3.9 | Table-3:- (Limit of Bacterial Colonies) |  |
|  | Grade; Alert; Action; Specification. A; <1; <1; <1. B; 3; 4; 5. C; 15-19; 20-24; 25. |
| 5.3.10 | Frequency:- Monthly ± 3 days. |  |
| 5.4 | Swab Test of Primary Sterile Material of Poly Bag in Aseptic areas of Ophthalmic Department, Drop Department, Veterinary Department :- |  |
| 5.4.1 | Prepare the Soyabean casein digest agar plates as per SOP No. QAMI18. Use 90 mm petri plates. |  |
| 5.4.2 | Prepare Normal saline solution and dispense 10 ml into 18 x 150 mm tubes and sterilize to autoclave at 15 lbs pressure and 121C for 20 minutes. |  |
| 5.4.3 | Mop the petri plates and Normal saline tubes from outside with 70% v/v Isopropyl Alcohol and label the petri plates indicating the surfaces to be tested as per specified in Annexure - XIV. |  |
| 5.4.4 | Use sterile swab of Sterile cotton, Dip the swab in sterile Normal saline solution. Remove excess solution from swab by pressing on side of tube. Take a swab 10×10 cm2 area as per Fig 1st and Fig 2nd from each surface of poly bag. Sample according to sampling plan shown in Annexure - XIV. |  |
|  | Fig: 1 (Direction of swab) Fig: 2 |
| 5.4.5 | Table 4:- (Limit of Bacterial Colonies) |  |
|  | Environment; Alert; Action; Specification. 1st bag inner side; <1; <1; <1. 2nd bag inner side; 3; 4; 5. |
| 5.4.6 | The 1st poly bag is the poly bag which is in direct contact with the sterile packing material and 2nd poly bag is the polybag which covers the 1st poly bag. |  |
| 5.4.7 | Mop the tested surfaces with 70% v/v Isopropyl alcohol. |  |
| 5.4.8 | Streak the swab on surface of Soyabean Casein Digest Agar in microbiology lab. |  |
| 5.4.9 | Incubate the petri plates at 20-250C temperature for 72 hours (3 days). After completion of 72 hours, transfer all petri plates at 30-350C for 48 hours (2 days) in inverted position. |  |
| 5.4.10 | After incubation, count the number of colonies and record the results in specified format (Annexure - XIV). |  |
| 5.4.11 | If the count lies in the Alert / Action limit as specified in the Table-4 & Table-2, microbiologist shall show the plates to Microbiology Head. It should be informed to QA department for further action through ‘Warning Letter’ as per Annexure - XX. |  |
| 5.4.12 | Frequency: Monthly ± 3 days |  |
| 5.5 | Swab Test of Sterile Equipment in Aseptic area of Ophthalmic Department, Drop Department and Veterinary Department :- |  |
| 5.5.1 | Prepare the Soyabean casein digest agar plates as per SOP No. QAMI18. Use 90 mm petri plates. |  |
| 5.5.2 | Prepare Normal saline solution and dispense 10 ml into 18 x 150 mm tubes and sterilize to autoclave at 15 lbs. pressure and 121C for 20 minutes. |  |
| 5.5.3 | Mop the petri plates and Normal saline tubes from outside with 70% v/v Isopropyl Alcohol and label the petri plates indicating the surfaces to be tested as per specified in Annexure - XV. |  |
| 5.5.4 | Use sterile swab of Sterile cotton, Dip the swab in sterile Normal saline solution. Remove excess solution from swab by pressing on side of tube. Take a Swab as per Fig 3rd and Fig 4th. Sample according to sampling plan shown in Annexure - XV. |  |
| 5.5.5 | Fig: 3 (Direction of swab) Fig: 4 |  |
| 5.5.6 | Table 5:- (Limit of Bacterial Colonies) |  |
|  | Grade; Alert; Action; Specification. A; <1; <1; <1. |
| 5.5.7 | Follow the same procedure from step 5.4.7 to 5.4.9. |  |
| 5.5.8 | After incubation count the number of colonies and record the results in specified format (Annexure - XV). |  |
| 5.5.9 | If the count lies in the Alert / Action limit as specified in the Table-5 & Table-2, microbiologist shall show the plates to Microbiology Head. It should be informed to QA department for further action through ‘Warning Letter’ as per Annexure - XX. |  |
| 5.5.10 | Frequency: Monthly ± 3 days |  |
| 5.6 | Contact Plate Test of Personnel Hygiene :- |  |
| 5.6.1 | Prepare the Dey-Engley Neutralizing agar as per SOP No. QAMI18. Use 55 mm (RODAC) petri plates. |  |
| 5.6.2 | Label the petri plates indicating the surfaces to be tested as specified in Annexure - XVI. |  |
| 5.6.3 | Aseptically transfer the plates to respective area, where the personnel’s monitoring is to be carried out. |  |
| 5.6.4 | Aseptically open the contact plates and gently touch on the sampling surfaces (like Elbow, Knee, Chest and Forehead) as mentioned in respective formats. |  |
| 5.6.5 | Clean the tested surfaces with 70% v/v Isopropyl alcohol. |  |
| 5.6.6 | Incubate the petri plates at 20-250C temperature for 72 hours (3 days). After completion of 72 hours, transfer all petri plates at 30-350C for 48 hours (2 days) in inverted position. |  |
| 5.6.7 | After incubation, count the number of colonies and record the results in specified format (Annexure - XVI). |  |
| 5.6.8 | If the count lies in the Alert / Action limit as specified in the Table-6 & Table-2, microbiologist shall show the plates to Microbiology Head. It should be informed to QA department for further action through ‘Warning Letter’ as per Annexure - XX. |  |
| 5.6.9 | Table 6:- (Limit of Bacterial Colonies) |  |
|  | Grade; Alert; Action; Specification. A; <1; <1; <1. B; 3; 4; 5. |
| 5.6.10 | Frequency:- Daily. |  |
| 5.6.11 | Note- Personnel Hygiene shall be done in Grade-B area at the end of activity. |  |
| 5.7 | Finger Dab Test :- |  |
| 5.7.1 | Prepare two plates of Soyabean Casein Digest Agar for each person (one for right hand and one for left hand). Each person should place all five fingers of right hand in one plate and all five fingers of left hand in another plate. |  |
| 5.7.2 | Transfer both the plates in Microbiology lab for incubation. |  |
| 5.7.3 | Incubate the petri plates at 20-250C temperature for 72 hours (3 days). After completion of 72 hours, transfer all petri plates at 30-350C for 48 hours (2 days) in inverted position and record the results as per Annexure - XVII. |  |
| 5.7.4 | If the count lies in the Alert / Action limit as specified in the Table-7 & Table-2, microbiologist shall show the plates to Microbiology Head. It should be informed to QA department for further action through ‘Warning Letter’ as per Annexure - XX. |  |
| 5.7.5 | Table 7:- (Limit of Bacterial Colonies) |  |
|  | Environment; Alert; Action; Specification. Personnel fingers (Five fingers) (Grade A); <1; <1; <1. Personnel fingers (Five fingers) (Grade B); 3; 4; 5. |
| 5.7.6 | Frequency: Daily. |  |
| 5.7.7 | Finger Dab Test is done in Grade-A or Grade-B area at the end of activity. |  |
| 5.8 | Media Controls :- |  |
| 5.8.1 | For Negative control take one petri plate of Soyabean Casein digest Agar and incubate the plate at 20-250C for 72 hours (3 days). After completion of 72 hours, transfer the plates at 30-350C for 48 hours (2 days) in inverted position. |  |
| 5.8.2 | For positive control take one petri plate of Soyabean Casein digest Agar and streak one Bacterium as per below Table-8 and incubate petri plate at 30-35°C for 24 to 48 hours. Rotate the organism as per Frequency mention in below Table-8:- |  |
| 5.8.3 | Table 8:- (Bacteria for Positive Control) |  |
|  | Name of Bacteria; Frequency. P. aeruginosa ATCC 9027; 01st to 10th date of month. S. aureus ATCC 6538; 11th to 20th date of month. Bacillus subtilis ATCC 6633; 21st to 31st date of month. |
| 6.0 | ANNEXURES:- |  |
| 6.1 | Annexure-I A : Microbial Monitoring of Ophthalmic Department |  |
| 6.2 | Annexure-I B : Microbial Monitoring of Ophthalmic Department (Filling LAF) |  |
| 6.3 | Annexure-II : Microbial Monitoring of Ophthalmic Area |  |
| 6.4 | Annexure-III A : Microbial Monitoring of Veterinary Department |  |
| 6.5 | Annexure-III B : Microbial Monitoring of Veterinary Department (Filling LAF) |  |
| 6.6 | Annexure-IV : Microbial Monitoring of Veterinary Area |  |
| 6.7 | Annexure-V : Microbial Monitoring of Microbiology Department |  |
| 6.8 | Annexure-VI A : Microbial Monitoring of Drop Department |  |
| 6.9 | Annexure-VI B : Microbial Monitoring of Drop Department (Filling LAF) |  |
| 6.10 | Annexure-VII A : Microbial Monitoring of Eye Ointment Department |  |
| 6.11 | Annexure-VII B : Microbial Monitoring of Eye Ointment Department (Filling LAF) |  |
| 6.12 | Annexure-VIII : Microbial Monitoring of Drop and Ointment Area |  |
| 6.13 | Annexure-IX : Microbial Monitoring of Microbiology Department by Contact Plate Method |  |
| 6.14 | Annexure-X : Microbial Monitoring of Ophthalmic Department by Contact Plate Method |  |
| 6.15 | Annexure-XI : Microbial Monitoring of Veterinary Department by Contact Plate Method |  |
| 6.16 | Annexure-XII : Microbial Monitoring of Drop Department by Contact Plate Method |  |
| 6.17 | Annexure-XIII : Microbial Monitoring of Ointment Department by Contact Plate Method |  |
| 6.18 | Annexure-XIV : Microbial Monitoring of Primary Packing Material by Swab Test |  |
| 6.19 | Annexure-XV : Microbial Monitoring of Sterile Equipment by Swab Test |  |
| 6.20 | Annexure-XVI : Microbial Monitoring of Personnel Hygiene |  |
| 6.21 | Annexure-XVII : Microbial Monitoring of Personnel Fingers |  |
| 6.22 | Annexure-XVIII: Microbial Monitoring of Sampling and Dispensing Area |  |
| 6.23 | Annexure-XIX: Microbial Monitoring of Manufacturing and Filling Area |  |
| 6.24 | Annexure-XX : Warning Letter |  |
| 7.0 | REFERENCES:- |  |
| 7.1 | WHO TRS Annexure 6. |  |
| 7.2 | Schedule M. |  |
| 7.3 | USP <1116> |  |
| 8.0 | REVISION HISTORY:- |  |
| Sr. No.; Revision No.; Date of Revision; SOP No.; Supersedes No.; Reason for Revision. 13; 13/12/2022; QAMI03-13; QAMI03-12; - Change in Firm Name from “Indiana Ophthalmics” to “Indiana Ophthalmics LLP”. - Addition of Scope, Annexures, References and Revision History as Section 2.0, 6.0, 7.0 and 8.0 respectively in the SOP. - Step 5.1.6.2 updated by adding that Settle plates in Grade-A filling area must be exposed during entire filling activity.. 14; 19/03/2023; QAMI03-14; QAMI03-13; - Updation of Plate No. and Location Name in Annexure-III and Annexure-IV.. 15; 18/07/2023; QAMI03-15; QAMI03-14; - Updation of Annexure-VIA and Annexure-VIB by adding the provision of exposing two plates under drop filling LAF.. 16; 19/07/2024; QAMI03-16; QAMI03-15; - Step 5.1.12 updated by adding provision to perform microbial monitoring in case if area remains shut down for more than 2 consecutive days. - Addition of doer-checker approach in annexures by adding provision of “Plates Observed By” and “Plates Verified By” in Annexures. - Addition of Annexure-XVIII (Microbial Monitoring of Sampling and Dispensing Area) and Annexure-XIX (Microbial Monitoring of Manufacturing and Filling Area).. |
| 17; 19/11/2024; QAMI03-17; QAMI03-16; - Addition of Step 5.8 for Media Controls. - Updation of Annexure-II by removing the plate exposure location of sampling and dispensing area.. 18; 22/08/2025; QAMI03-18; QAMI03-17; - Updation of Plate No. and Plate Location in Annexure-V and Updation of sampling location for contact plates in Annexure-IX as per upgraded new microbiology lab.. |